## Self-assessment checklist B105
Bulletin 105 Compliance self-assessment
Location: | Insert Name of entity and location | Assessment completed by: | Insert Names | Date: | Insert date of initial assessment
|  | Status reviewed by: | Insert Names | Date: | Insert date of review
|  | Status review: |  | Date: | Insert date of next planned review
| Bulletin 105 requirements | Is there a Gap | Action To Close Gap | Responsible Person | Planned Start Date | Planned Finish Date | Status Pending or Closed | Comments
Filter Vessels, elements and accessories
1 | All 2" and 6" filter monitors operate at below 15psi or 1.0 bar at maximum achievable flow
2 | All 2" and 6" filter monitors are compliant to EI1583 7th Edition
3 | All stock of filter monitors checked and purged of non EI1583 7th edition compliant elements
4 | Operational data plates changed where manufacturer or brand of elements changed
5 | All monitor vessels have been reviewed for conversion to EI1581 6th edition FWS
6 | Conversion data plate & new operational data plate fitted where a monitor vessel is converted to EI1581 6th ed FWS
7 | Where monitor vessels with in-to-out elements cannot be converted to EI1581 they have been replaced by FWS or retired
8 | All filter monitor systems previously converted from FWS have been reconverted back to FWS.
9 | Conversion plate removed where a previously converted vessel is reconverted to FWS
10 | DP limiting devices are installed and set to max 15psi (1.0 bar) on all fuelling equipment fitted with filter monitors
11 | All DP limiting device reset systems are controlled by a method which may only be used by maintenance staff or supervisor/management
12 | All hose end strainers of fuelling equipment are 100 Mesh size
13 | All filter monitor systems not controlled by EI1583 or EI1596 (such as single element systems) have been assessed as: - Fit for purpose - Not permitting detectable SAP migration - Operated in compliance with manufacturer recommendations. - Their use is limited to a maximum operational DP of 15psi or 1.0 bar
Element Change process & commissioning procedure
1 | Has the documented procedure for commissioning filter elements been updated in line with Bulletin 105 requirements including: - Fuel flow commenced and maintained at Maximum Achievable flow rate for 5 minutes? - 4 stop/starts performed using Deadman within the 5 minute timeframe and at 1 minute intervals - Bulletin 105 procedure applied for hose end strainer cleaning after all filter monitor commissioning
2 | Have all relevant staff been trained on the updated procedure?
3 | Is the updated commissioning procedure also used for over wing circuits?
Hose end strainer inspection
1 | A preferred cleaning method has been established (compressed air, jet fuel wash bottle or brush cleaning, as per bulletin) - specify which method in comments column.
2 | Has the written procedure for hose end strainer inspection and cleaning been updated as required to reflect the preferred cleaning method?
3 | Does the written procedure include the requirement to vigorously agitate the hose end strainer in fuel for 1minute prior to cleaning?
4 | Does the written procedure include the requirement to lift and lower the hose end strainer into and out of the fuel to back flush any debris into the fuel bucket?
5 | Does the written procedure include the requirement to rinse the strainer in fresh fuel before being returned to service?
6 | All relevant staff have been trained in the requirements of the procedure for hose end strainer inspection and cleaning.
MOC, procedures and training
1 | MOC completed covering bulletin 105 implementation
2 | Local procedures, manuals, forms and training documents updated
3 | Training provided to all relevant staff on actions defined in Bulletin 105
4 | Filter monitors never operated outside qualified design envelope
5 | Similarity certificate obtained from Manufacturer where a vessel is converted/reconverted to FWS
6 | Venturi checked and re-adjusted where necessary when a 60 mesh strainer has been replaced with a 100 mesh strainer
7 | All DP switches checked under flow conditions for correct activation at 15 psi
8 | Filters never moved to a lower flow rate application to extend service life when high DP (15psi) is reached
9 | New build specifications revised to consider bulletin 105 actions when procuring new vehicles
10 | DP measurement and recording procedures (graphs) adopted in line with bulletin 113, DP correction not recommended
Ongoing validation & actions
1 | Any recorded quality issues with 7th edition monitors
2 | Incidents reported and investigated with manufacturer
3 | Any recorded instances of high DP activation of limiting switches
4 | Were reset procedures followed correctly, reason for activation identified and recorded
5 | Any filter vessels reaching max changeout DP before scheduled change, cause identified & rectified on investigation?
6 | Frequent DP switch activation on any individual vehicles
7 | Cause identified and action taken to rectify where appropriate
8 | Debris found during hose end strainer cleaning (either after commissioning or regular hose end inspection)
9 | Causes established, recorded and corrective action taken
10 | History of hose end strainers found to be damaged? Incidents recorded and strainer repaired or replaced?
The procedures and practices presented in this document are best practice recommendations only and Joint Inspection Group Limited (“JIG”) makes no claim or warranty whatsoever as to their completeness or suitability.
Any users of this document and the information set out in it use it entirely at their own risk. For the full terms and conditions concerning use of this Document, please refer to https://www.jig.org/legal-copyright/
Rev 2 Jan22
GAP
No Gap

## Task card Test rig method
Filter commissioning & Hose end strainer cleaning Task card-Test rig
| Step | Site Specific requirements
Preparation
Gather required materials and tools
1 | Record forms and pen | ×
2 | PPE to be worn in accordance with site and company policies
3 | Access confirmed to test rig and operator informed of commissioning activities
4 | Tools to remove hose end strainer from nozzle
5 | Clean bucket with bonding cable containing approximately 4' or 10-11cm of contaminant free fuel
6 | Compressed air source OR
7 | Suitable jet fuel wash bottle containing clean jet fuel OR
8 | Clean fine stiff haired 1/4' or 6-7cm brush
9 | Suitable hose end drain down facility
10 | Clean surface available to tap out any hose end contaminants
Filter commissioning
1 | Bond vehicle to test rig
2 | Connect according to locally agreed connection sequence
3 | Zero delivery meter and record totalizer reading
4 | Open test rig valve
5 | Open vehicle valve slowly to control fill rate
6 | Depress Deadman to initiate fuel flow
7 | Fill vessel slowly to prevent static discharge
8 | Ensure all air is purged from system (check air eliminator or sho-flo)
9 | Begin flowing fuel at the maximum achievable flow rate designated for the vehicle/vessel (5 minute timeframe required)
10 | Using the Deadman perform at least 4 stop/starts at 1 minute intervals within this time-frame
11 | Close delivery valve
12 | Close test rig valve
13 | Record totalizer reading
14 | Disconnect from test rig according to locally agreed disconnection procedure
Hose end strainer inspection (following filter commissioning or routine check)
Strainer removal
1 | Bond Vehicle to drain down facility
2 | Connect coupling to drain down facility
3 | Open poppet valve and drain product
4 | Detach nozzle from hose or open ball valve dependant on nozzle design
5 | Ensure any residual fuel in hose or nozzle is drained as far as possible
6 | Handle hose so that any debris contained in the hose is drained into the hose end strainer
7 | Keep nozzle upright at 45 degrees to ensure any contaminants are retained inside the hose end strainer
8 | Follow manufacturer procedure to remove the strainer from housing
9 | Examine strainer carefully for signs of damage, corrosion or defect
10 | Replace strainer with a new one if any damage observed
11 | Examine condition of strainer retaining circlip
Strainer inspection
1 | Invert strainer over a clean surface and tap to dislodge any contaminants
2 | Document any debris found
3 | Completely submerge the strainer in clean fuel
4 | Agitate vigorously whilst submersed in the fuel
5 | Maintain agitation for 1 minute
6 | Keeping strainer below top level of container, successively lift and lower it in and out of the fuel (cone up) to back flush any debris into the bucket
7 | Repeat this process 10 times
8 | Dispose fuel in bucket if not further required (compressed air cleaning method) as it may contain SAP or other contaminants- DO NOT RETURN TO SERVICE!
9 | Continue to designated strainer cleaning method
Strainer cleaning
Method 1-Compressed air cleaning (preferred)
1 | Use a lubricant free compressed air source to blow any debris from the 'clean side' to the 'dirty side' over a bucket to capture any debris
2 | Systematically ensure the air jet passes over the entire surface of the strainer
3 | Repeat entire process at least 3 times
4 | Examine strainer cleanliness and repeat if necessary
5 | Document and dispose of any contaminants and fuel in the bucket in accordance with site hazardous waste disposal processes, it may contain SAP or other contaminants- DO NOT RETURN TO SERVICE!
Method 2-Jet fuel wash bottle method
1 | Use the jet fuel bottle to wash any debris from the 'clean side' to the 'dirty side' into the bucket of used fuel.
2 | Systematically ensure the stream of fuel washes over the entire surface of the strainer
3 | Repeat entire process at least 3 times
4 | Examine strainer cleanliness and repeat if necessary
5 | Dispose of any fuel and contaminants into the bucket
6 | Dispose of used fuel in bucket in accordance with site hazardous waste disposal processes, it may contain SAP or other contaminants- DO NOT RETURN TO SERVICE!
Method 3-Brush cleaning method
1 | Use the brush to 'stipple' the downstream 'clean side' of the hose
2 | Loosen any potential debris pushing it towards the upstream 'dirty side'
3 | Cover the entire surface of the strainer with the brush and stippling process
4 | Wet the brush in clean fuel
5 | Start brushing at the internal point of the strainer
6 | Brush any debris out towards the strainer rim
7 | Re-wet brush frequently
8 | Ensure no brush bristles are dislodged and caught in hose end strainer
9 | Examine strainer cleanliness and repeat if necessary
10 | Dispose of any fuel and contaminants into the bucket
11 | Dispose of used fuel in bucket in accordance with site hazardous waste disposal processes, it may contain SAP or other contaminants- DO NOT RETURN TO SERVICE!
Re-installation of hose end strainer and re-commissioning
1 | Rinse strainer in fresh fuel
2 | Re-inspect hose end strainer visually again for cleanliness and damage
3 | Re-install hose end strainer in line with manufacturer instructions
4 | Re-assemble swivel or ball valve depending on design
5 | Check integrity of coupling by pressurizing to working pressure
6 | If no leaks found return to service
7 | Complete required record forms
The procedures and practices presented in this document are best practice recommendations only and Joint Inspection Group Limited (“JIG”) makes no claim or warranty whatsoever as to their completeness or suitability.
Any users of this document and the information set out in it use it entirely at their own risk. For the full terms and conditions concerning use of this Document, please refer to https://www.jig.org/legal-copyright/
Rev 2 Jan22

## Task card Recirculation
Filter commissioning & Hose end strainer cleaning Task card-recirculation
| Step | Site Specific requirements
Preparation
Gather required materials and tools
1 | Record forms and pen | ×
2 | PPE to be worn in accordance with site and company policies
3 | Access confirmed to test rig and operator informed of commissioning activities
4 | Tools to remove hose end strainer from nozzle
5 | Clean bucket with bonding cable containing approximately 4' or 10-11cm of contaminant free fuel
6 | Compressed air source OR
7 | Suitable jet fuel wash bottle containing clean jet fuel OR
8 | Clean fine stiff haired 1/4' or 6-7cm brush
9 | Suitable hose end drain down facility
10 | Clean surface available to tap out any hose end contaminants
Filter commissioning
1 | Follow local procedures to ensure sufficient ullage in vehicle for recirculation
2 | Connect delivery hose(s) to bottom loading or recirculation point
3 | Zero delivery meter and record totalizer reading
4 | Open vehicle valve slowly to control fill rate
5 | Depress Deadman to initiate fuel flow
6 | Open recirculation or bottom loading valve
7 | Operate vehicle valve to control fill rate
8 | Fill vessel slowly to prevent static discharge
9 | Ensure all air is purged from system (check air eliminator or sho-flo)
10 | Begin flowing fuel at the maximum achievable flow rate designated for the vehicle/vessel (5 minute timeframe required)
11 | Using the Deadman perform at least 4 stop/starts at 1 minute intervals within this time-frame
12 | Close delivery valve
13 | Disconnect hose(s)
14 | Record totalizer reading
Hose end strainer inspection (following filter commissioning or routine check)
Strainer removal
1 | Bond Vehicle to drain down facility
2 | Connect coupling to drain down facility
3 | Open poppet valve and drain product
4 | Detach nozzle from hose or open ball valve dependant on nozzle design
5 | Ensure any residual fuel in hose or nozzle is drained as far as possible
6 | Handle hose so that any debris contained in the hose is drained into the hose end strainer
7 | Keep nozzle upright at 45 degrees to ensure any contaminants are retained inside the hose end strainer
8 | Follow manufacturer procedure to remove the strainer from housing
9 | Examine strainer carefully for signs of damage, corrosion or defect
10 | Replace strainer with a new one if any damage observed
11 | Examine condition of strainer retaining circlip
Strainer inspection
1 | Invert strainer over a clean surface and tap to dislodge any contaminants
2 | Document any debris found
3 | Completely submerge the strainer in clean fuel
4 | Agitate vigorously whilst submersed in the fuel
5 | Maintain agitation for 1 minute
6 | Keeping strainer below top level of container, successively lift and lower it in and out of the fuel (cone up) to back flush any debris into the bucket
7 | Repeat this process 10 times
8 | Dispose fuel in bucket if not further required (compressed air cleaning method) as it may contain SAP or other contaminants- DO NOT RETURN TO SERVICE!
9 | Continue to designated strainer cleaning method
Strainer cleaning
Method 1-Compressed air cleaning (preferred)
1 | Use a lubricant free compressed air source to blow any debris from the 'clean side' to the 'dirty side' over a bucket to capture any debris
2 | Systematically ensure the air jet passes over the entire surface of the strainer
3 | Repeat entire process at least 3 times
4 | Examine strainer cleanliness and repeat if necessary
5 | Document and dispose of any contaminants and fuel in the bucket in accordance with site hazardous waste disposal processes, it may contain SAP or other contaminants- DO NOT RETURN TO SERVICE!
Method 2-Jet fuel wash bottle method
1 | Use the jet fuel bottle to wash any debris from the 'clean side' to the 'dirty side' into the bucket of used fuel.
2 | Systematically ensure the stream of fuel washes over the entire surface of the strainer
3 | Repeat entire process at least 3 times
4 | Examine strainer cleanliness and repeat if necessary
5 | Dispose of any fuel and contaminants into the bucket
6 | Dispose of used fuel in bucket in accordance with site hazardous waste disposal processes, it may contain SAP or other contaminants- DO NOT RETURN TO SERVICE!
Method 3-Brush cleaning method
1 | Use the brush to 'stipple' the downstream 'clean side' of the hose
2 | Loosen any potential debris pushing it towards the upstream 'dirty side'
3 | Cover the entire surface of the strainer with the brush and stippling process
4 | Wet the brush in clean fuel
5 | Start brushing at the internal point of the strainer
6 | Brush any debris out towards the strainer rim
7 | Re-wet brush frequently
8 | Ensure no brush bristles are dislodged and caught in hose end strainer
9 | Examine strainer cleanliness and repeat if necessary
10 | Dispose of any fuel and contaminants into the bucket
11 | Dispose of used fuel in bucket in accordance with site hazardous waste disposal processes, it may contain SAP or other contaminants- DO NOT RETURN TO SERVICE!
Re-installation of hose end strainer and re-commissioning
1 | Rinse strainer in fresh fuel
2 | Re-inspect hose end strainer visually again for cleanliness and damage
3 | Re-install hose end strainer in line with manufacturer instructions
4 | Re-assemble swivel or ball valve depending on design
5 | Check integrity of coupling by pressurizing to working pressure
6 | If no leaks found return to service
7 | Complete required record forms
The procedures and practices presented in this document are best practice recommendations only and Joint Inspection Group Limited (“JIG”) makes no claim or warranty whatsoever as to their completeness or suitability.
Any users of this document and the information set out in it use it entirely at their own risk. For the full terms and conditions concerning use of this Document, please refer to https://www.jig.org/legal-copyright/
Rev 2 Jan22